## Common
BVN Revit Family | Application | Doorset ie overall frame (actual in brackets) | Leaf Widths | Min clear opening | Complies with | Non- compliances | Remarks
SINGLE DOORS
D120 a b c a-p | Non- clinical areas only (min. 700 clear. 750 clear if non-fire rated hinged only) · ambulant disabled sanitary compartments for public and staff (ie non-patient) · used on FHR cupboards in MCR (and NBH including FHR cupboards; suits 960 x 2220 conc openings on core) · can be use for NFR hinged 750 clear door where wheelchair access is not required incl access to ambulant disabled WCs · NBH: public/ staff WCs EDB Cupboards – single leaf | 910 nom (902 hinged/ 908 FR pivot actual) | 820 | 734 transom closer pivot 743 WC pivot + hinged FD 761 NFR hinged | BCA cl. D1.6 (f) (v) re sanitary compartment AS 1428.1-2009 cl. 16.3 re 700 clear opening for ambulant disabled sanitary compartment BCA cl. D1.6 (f)(v) re 750 clear opening if NFR hinged | HFG RDS/RDS for Staff WC, Staff Showers and Public WCs require 850 clear | Need to consider if we need to size set to permit pivot with retractable stop Consider decreasing to min.790 std leaf if tight for space NBH: D120a-18 = 1790h leaf for B01 FHR cupboard under stair
D130 a b c d | Non- clinical areas only (min. 750 clear. 850 clear if non-fire rated hinged only) (D150 preferred to D130 to ensure 850 clear in all configurations) · Non accessible areas · NFR wheelchair access eg offices, admin stores · as non-fire rated door across corridors · NBH: interview, meeting, offices, staff locker/ change, public/ staff access WC if hinged only (not pivot), clinical wkrms | 1010 nom (1002 hinged/ 1008 FR pivot actual) | 920 | 834 transom closer pivot 843 WC pivot + hinged FD 861 NFR hinged | BCA cl. D1.6 (f)(v) re 750 clear opening AS 1428.1 cl.13.2 re 850 clear opening if NFR hinged only | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs AS 1428.1 cl.13.2 re 850 clear opening if WC pivot , pivot FD or hinged FD | NFR hinged door will achieve 850 clear, complying with AS 1428.1 WC pivot type to be used for inward opening sanitary compartment doors to avoid use of rising butt hinges (with hollow core doors) or closers If leaf is used, this will not always provide a min. 850 clearance under AS1428.1 Preference to use D150 below where possible. Otherwise will need to consider 940w leaf / 1030 set to ensure 850 clear in all circumstances ie transom pivot, WC pivot and fire door.
D150 a b c d a-p a+ peephole c + DGIV h | Clinical areas (min. 900 clear) · access by stretchers, wheeled bed stretchers, wheelchairs and handicapped persons including those using assistive devices patient WCs, patient showers, patient ensuites, patient change, consult rms in GPC and PCS. · access for small trolleys, wheelie bins eg DUs, CUs, beverage rooms, cleaners, ante rooms · NBH: OR/Sterile St, general stores, store/photocopy/ file, staff rms Non –clinical areas · wheelchair access eg offices, admin stores · access for small trolleys eg beverage rooms, cleaners · fire stairs · plant rooms | 1080 nom (1072 hinged/ 1078 FR pivot actual) | 990 | 904 transom closer pivot 913 WC pivot + hinged FD 931 NFR hinged | AS 1428.1 cl.13.2 re 850 clear opening HFG cl. 710.27.00 requires min. 900 clear for wheelchairs… HFG RDS/ RLS for Staff WC, Staff Showers and Public WCs (which require 850 clear HFG RDS/RDS typically require 910 clear for single leaf doors, except if transom closer used | Except for Staff WC, Staff Showers and Public WCs (which require 850 clear) HFG RDS/RDS typically require 910 clear for single leaf doors. Non-compliance for transom pivot configuration if used. | Assumes that no patient lifters/ hoists are used in these rooms NBH: h = high obs panel + DGIV, where u/s HOBS is at 1400 AFFL and is 200w NBH: m = MH obs panel, where u/s MOBS is at 1000 AFFL but is 300w (in lieu of 200w for SOBS)
DOUBLE DOORS
D210 a a + peephole | Double door – Non-fire rated, 40 thick leaves and hinged configuration only (min. 1200 clear if NRF and no closer on secondary leaf) · to bariatric and ICU Ensuites as per HFG RDS/ RLS\ · consult rms | 1380 nom for hinged only (1380 hinged/ 1388 FR pivot actual) | 955 + 340 (minimal leaf widths to give 1200/ 910 clearances would be 954 + 337 leaves) | FYI: 1188 hinged FD, (899 primary opening; 1380 set) 1204 NFR hinged, (911 primary opening) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. BCA cl.D3.2(e) re min.850 primary opening HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms HFG cl. 710.27.00 re 1000 for hoists and shower trolleys | HFG RDS/ RLS for rms requiring 1400 clear, 1350 clear eg Bathroom BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit | RNSH: NB. Bariatric bed is 1130 wide (add 100 for side rails ie 1230 wide) – check corridor width needed to suit turning circle. See email 10:27am on 24.11.08 JW to NL 1.07 – is a 1601 clear opening needed? Min. 450 secondary leaf required for slide arm closers. Wider leaf may be required for concealed closers that would probably be used in Mental Health for anti-ligature (540 for Dorma ITS 69) – check closer constraints for various types incl. RTS, ITS and TS and auto incl. sequencers. RNSH: had to use min.800+920 leaves to fit ITS closers and NE latches to PEC doors Min. WL of 530 where D = 900 in AS1428.1 requires min. 389w secondary leaf if hinged configuration assuming 100 nib, but this is too narrow for closer If sequencer is required, it will need to be integral with closers due to width of secondary leaf
D220 | Double door – Non-fire rated, 40 thick leaves and hinged configuration only | 1590 nom | 955 + 540 | FYI: 1320 transom closer pivot, (869 primary opening but 1588 set) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. | HFG RDS/ RLS for rms requiring 1400 clear. Non-compliance if pivot, transom pivot or FR hinged door configurations or if door leaves thicker then 45mm.
a | (min. 1400 clear if NRF) | (1580 hinged/ 1588 FR pivot actual) | (minimal NRF hinged leaf widths to give 1400/ 910 clearances would be 954 + 537 leaves) | FYI: 1388 hinged FD, (899 primary opening; 1580 set) | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit | 910 primary clear opening is required in certain HFG RDS/ RLS – not achieved if FR hinged or if transom pivot configuration | RNSH: NB. Bariatric bed is 1130 wide (add 100 for side rails ie 1230 wide) – check corridor width needed to suit turning circle. See email 10:27am on 24.11.08 JW to NL 1.07 – is a 1601 clear opening needed?
b | (D230 is preferred due to compliance as hinged FR or if thicker leaves) |  |  | 1404 NFR hinged, (911 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Min. 450 secondary leaf required for slide arm closers. Wider leaf may be required for concealed closers that would probably be used in Mental Health for anti-ligature (540 for Dorma ITS 69) – check closer constraints for various types incl. RTS, ITS and TS and auto incl. sequencers.
| · Horizontal exit in a patient care area under BCA min. 1250 clear |  |  |  | HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms |  | RNSH: had to use min.800+920 leaves to fit ITS closers and NE latches to PEC doors
| · access for hoists and shower trolleys | [5 empty] | Min. 720w leaf to fit transom closer, shear lock and reed switch (though achieved 620w on RNSH for door 07/1064)
| · access for stretchers, large trolleys, large equipment, beds but check std and bariatric beds esp. if off 1800 clear corr |  |  |  | HFG cl. 710.27.00 re 1000 for hoists and shower trolleys |  | Min. 725w leaves to fit auto swing door operator but may need to add additional width for EMLs.
| · patient bed rooms, patient assisted bathrooms | [5 empty] | Min. WL of 530 where D = 900 in AS1428.1 requires min. 389w secondary leaf if hinged configuration assuming 100 nib, but this is too narrow for closer
| · bed accessible rooms eg imaging rooms |  |  |  | HFG RDS/ RLS for rms requiring 1400 clear with 910 primary clear opening when hinged, NFR configuration |  | If sequencer is required, it will need to be integral with closers due to width of secondary leaf
Unlikely to suit bariatric beds
D230 | Double door (min. 1400 clear) | 1605 nom | 990 + 520 | 1335 transom closer pivot, (904 primary opening) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. | HFG RDS/ RLS for rms requiring 1400 clear. Non-compliance if transom closer configuration which is unlikely in these contexts.
a | · Horizontal exit in a patient care area under BCA min. 1250 clear | (1595 hinged/ 1603 FR pivot actual) |  | 1403 hinged FD, (934 primary opening) | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit |  | RNSH: NB. Bariatric bed is 1130 wide (add 100 for side rails ie 1230 wide) – check corridor width needed to suit turning circle. See email 10:27am on 24.11.08 JW to NL 1.07 – is a 1601 clear opening needed?
b | · access for hoists and shower trolleys |  |  | 1419 NFR hinged, (946 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Min. 450 secondary leaf required for slide arm closers. Wider leaf may be required for concealed closers that would probably be used in Mental Health for anti-ligature (540 for Dorma ITS 69) – check closer constraints for various types incl. RTS, ITS and TS and auto incl. sequencers.
c | · access for stretchers, large trolleys, large equipment, beds but check std and bariatric beds esp. if off 1800 clear corr |  |  |  | HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms |  | Min. 720w leaf to fit transom closer, shear lock and reed switch (though achieved 620w on RNSH for door 07/1064)
a + peephole | · patient bed rooms, patient assisted bathrooms | [5 empty] | Min. 725w leaves to fit auto swing door operator but may need to add additional width for EMLs.
| · bed accessible rooms eg imaging rooms |  |  |  | HFG cl. 710.27.00 re 1000 for hoists and shower trolleys |  | RNSH: had to use min.800+920 leaves to fit ITS closers and NE latches to PEC doors
| · NBH: consult, birthing rooms, disposal, general xray rm, equipment stores, ultrasound | [5 empty] | Min. WL of 530 where D = 900 in AS1428.1 requires min. 389w secondary leaf if hinged configuration assuming 100 nib, but this is too narrow for closer
[5 empty] | HFG RDS/ RLS for rms requiring 1400 clear with 910 primary clear opening, except if transom closers used |  | If sequencer is required, it will need to be integral with closers due to width of secondary leaf
Review for MCR: Unlikely to suit bariatric beds
D250 | EDB Cupboards | 1735 nom | 820+820 x 2140h | 1465 transom closer pivot, (834 primary opening)
|  | (1725 hinged/ 1733 FR pivot actual) |  | 1533 hinged FD, (768 primary opening)
1549 NFR hinged, (776 primary opening)
D260 | Double door (min. 1500 clear) | 1785 nom | 970 + 720 | 1515 transom closer pivot, (884 primary opening) | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts
a | · Suitable for use as door across 1800 clear corridor but will have 82.5mm nibs | (1775 hinged/ 1783 FR pivot actual) |  | 1583 hinged FD, (918 primary opening) |  |  | 910 primary clear opening not achieved for transom pivot configuration for 970w leaf.
| · Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms |  |  | 1599 NFR hinged, (926 primary opening)
| · To suit bed access off 1800 clear corridor but check suitability for bariatric beds | [5 empty] | (910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts.)
970 leaf is also used in D270 below
Min. 720w leaf to fit transom closer, shear lock and reed switch (though achieved 620w on RNSH for door 07/1064)
Min. 725w leaves to fit auto swing door operator but may need to add additional width for EMLs.
D265 | Double door (min. 1500 clear) | 1815 nom | 860 + 860 | 1545 transom closer pivot, (774 primary opening) | HFG RDS/ RLS for Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms | 910 primary clear opening is required in certain HFG RDS
h | Can only be use where exempt from BCA/ AS 1428.1 re 850 clear for accessibility unless door is automatic | (1805 hinged/ 1813 FR pivot actual) |  | 1613 hinged FD, (808 primary opening) |  | BCA cl.D3.2(e) re min.850 primary opening | Refer to BCA cl. D3.2(e) re automatic/ power operation may alleviate AS 1428.1 non-compliance.
| · NBH: OR, Sterile Stock Stores |  |  | 1629 NFR hinged, (816 primary opening)
D266 | NBH RDS nominates 920 + 920 for Procedure Rm, Endoscopy (achieves min. 1650 clear) | 1935 nom | 920 + 920 | 1664 transom closer pivot, (834 primary opening) |  | 910 primary clear opening is required in certain HFG RDS
a | · NBH: Procedure Rm, Endoscopy | (1925 hinged/ 1933 FR pivot actual) |  | 1733 hinged FD, (868 primary opening) |  | BCA cl.D3.2(e) re min.850 primary opening for transom pivot
b | · ITV Sterile Stock |  |  | 1749 NFR hinged, (876 primary opening)
· option for linen bays
D270 | Double door (min. 1765 clear) | 2035 nom | 970 + 970 | 1765 transom closer pivot, (884 primary opening) | HFG RDS/ RLS for Catheter Lab Procedure Rms and Angio Procedure Rms – check other specialist rms requiring 1600 clear | 910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts
a | · Suitable for use as door across 2100 clear corridor | (2025 hinged/ 2033 FR pivot actual) |  | 1833 hinged FD, (918 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Review for MCR: Does this suit bariatric beds?
b | · linen bays (preferred) |  |  | 1849 NFR hinged, (926 primary opening)
c | · HFG RDS/ RLS for Catheter Lab Procedure Rms and Angio Procedure Rms – check other specialist rms requiring 1600 clear | [5 empty] | Would need 990w primary leaf to achieve 910 clear for transom pivot
d
910 primary clear opening not achieved for transom pivot configuration for 970w leaf.
(910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts.)
Min. 720w leaf to fit transom closer, shear lock and reed switch (though achieved 620w on RNSH for door 07/1064)
Min. 725w leaves to fit auto swing door operator but may need to add additional width for EMLs.
D278 | Double door (min. 1900 clear) | 2175 nom | 1040 + 1040 | 1905 transom closer pivot, (914 primary opening) | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS
| · For Link Bridge for max clear opening on esp. hold open doors | (2165 hinged/ 2173 FR pivot actual) |  | 1973 hinged FD, (988 primary opening)
1989 NFR hinged, (996 primary opening)
D280 | Double door | 2335 nom | 1120 + 1120 | 2065 transom closer pivot, (994 primary opening) | BCA cl.D3.2(e) re min.850 primary opening
| · for major corridors | (2325 hinged/ 2333 FR pivot actual) |  | 2133 hinged FD, (1068 primary opening)
2149 NFR hinged, (1076 primary opening)
D285 | Double door (for max. 1200 leaves) | 2495 nom | 1200 + 1200 | 2225 transom closer pivot, (1074 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Min 45 thick to minimise bowing
| · for major corridors | (2485 hinged/ 2493 FR pivot actual) |  | 2293 hinged FD, (1148 primary opening)
2299 based on 45 thick NFR hinged, (1151 primary opening)

## UnCommon
BVN Revit Family | Application | Doorset ie overall frame (actual in brackets) | Leaf Widths | Min clear opening | Complies with | Non- compliances | Remarks
SINGLE DOORS
(old RNSH D10) | Non- clinical areas only (less than 750 clear) · ambulant sanitary compartments for public and staff (ie non-patient) | 810 nom (802 hinged/ 808 FR pivot actual) | 720 | 634 transom closer pivot 643 WC pivot + hinged FD 661 NFR hinged | BCA cl. D1.6 (f) (v) re sanitary compartment | AS 1428.1-2009 cl. 16.3 re 700 clear opening for ambulant disabled sanitary compartment | WC pivot type to be used for inward opening sanitary compartment doors to avoid use of rising butt hinges (with hollow core doors) or closers Review for MCR: is this too narrow?
(old RNSH FHR-a) | FHR cupboard - Type A · 35 thick leaf | 890 nom (892 NFR hinged actual) | 810 | 756 |  |  | Not to be used for habitable spaces ie only in “access panel” applications Review for MCR: size tbc; would be preferable to have a std leaf used elsewhere in the project Consider using 720 or 820 leaf ( ie D10 or D11)
| 4-Brick opening (970 brick opening) Allow 10mm tolerance each side · Non-compliant for wheelchair access | 950 nom (947 hinged) | 865 | 788 hinged FD 806 NFR hinged | BCA cl. D1.6 (f)(v) re 750 clear opening | AS 1428.1 cl.13.2 re 850 clear opening HFG cl. 710.27.00 requires min. 900 clear for wheelchairs | Based on FFL being 40 below top of base course (to allow for sill and sub sill), 20mm at head for steel lintel and building tolerance · 25C high = 2153, achieves 2030 clear door opening ht for FD · 26C high = 2239, achieves 2116 clear door opening ht for FD · 27C high = 2324, achieves 2201 clear door opening ht for FD · 28C high = 2410, achieves 2287 clear door opening ht for FD
D132 | Non- clinical areas only (min. 850 clear. (D150 preferred to D130 to ensure 900 clear to align with clinical applications) · accessible areas · NBH-specific doors to core and carpark for personnel access (suits conc opening of 1080 x 2220h) | 1030 nom (1022 hinged/ 1028 FR pivot actual) | 940 | 854 transom closer pivot 863 WC pivot + hinged FD 881 NFR hinged | BCA cl. D1.6 (f)(v) re 750 clear opening AS 1428.1 cl.13.2 re 850 clear | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs
De140 | 4+1/2 Brick opening (1090 brick opening) Allow 10mm tolerance each side Non-compliant for wheelchair access | 1070 nom (1062 hinged) | 980 | 903 hinged FD 921 NFR hinged | BCA cl. D1.6 (f)(v) re 750 clear opening AS 1428.1 cl.13.2 re 850 clear opening HFG cl. 710.27.00 requires min. 900 clear for wheelchairs |  | Based on FFL being 40 below top of base course (to allow for sill and sub sill), 20mm at head for steel lintel and building tolerance · 25C high = 2153, achieves 2030 clear door opening ht for FD · 26C high = 2239, achieves 2116 clear door opening ht for FD · 27C high = 2324, achieves 2201 clear door opening ht for FD · 28C high = 2410, achieves 2287 clear door opening ht for FD
| 5-Brick opening (1210 brick opening) | 1190 nom | 1108 | 1046 hinged FD | BCA cl. D1.6 (f)(v) re 750 clear opening |  | Based on FFL being 40 below top of base course (to allow for sill and sub sill), 20mm at head for steel lintel and building tolerance
|  | (1187 hinged) |  | 1028 NFR hinged | AS 1428.1 cl.13.2 re 850 clear opening |  | · 25C high = 2153, achieves 2030 clear door opening ht for FD
| Allow 10mm tolerance each side |  |  |  | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs |  | · 26C high = 2239, achieves 2116 clear door opening ht for FD
| · compliant for wheelchair access | [5 empty] | · 27C high = 2324, achieves 2201 clear door opening ht for FD
· 28C high = 2410, achieves 2287 clear door opening ht for FD
D180 | Mental Health | 1280 nom | 1185 | 1099 transom closer pivot | AS 1428.1 cl.13.2 re 850 clear opening |  | Unlikely to use this with transom pivot
a | (min.1100 clear) | (1267 hinged/ 1273 FR pivot actual) |  | 1108 WC pivot (for 40 thick leaf) + hinged FD | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs… |  | Consider min. 45 thick to minimise bowing for wide leaf
a-p |  | NB. 1280 allows for thicker prop. 52 thick leaf for MH |  | 1126 NFR hinged (for 40 thick leaf) |  |  | NBH: m-p = MH observation panel = MOBS + DGIV, where MOBS is sim to SOBS but 300w (in lieu of 200w)
m-p | [6 empty] | Review leaf/ set size if Hipac hardware is used
D181 | Comms Rooms | [5 empty] | As per D180 but 2240h leaf
Added as change from Tender D231 (see below) at TUG request.
Provides min. 1000w clear nominated by WGE/ Stowe at TUG but should be confirmed
D190 | For single leaf hinged fire door as Horizontal Exit required to be 1250 clear min. | 1420 nom | 1330 | 1244 transom closer pivot | AS 1428.1 cl.13.2 re 850 clear opening
|  | (1412 hinged/ 1418 FR pivot actual) |  | 1253 WC pivot + hinged FD | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs…
|  |  |  | 1271 NFR hinged | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit
(D192) | IPU Bed Rooms with 1370w NFR leaves with hospital hinges | 1455 nom tbc | 1370 | 1346 tbc for 45 thick leaf | AS 1428.1 cl.13.2 re 850 clear opening |  | Requirement for LOBS in CCU, SOBS generally
a | For NBH to Healthscope requirements incl. hospital hinges | (1370 + 38 +38 +3 + 3 = 1452 actual tbc) |  |  | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs…
b |  |  |  |  | HSL/ LC requirement for 1340 clear w doors (see 4.5.15 correspondence re NBH-HSC-CORR-00069 NBH -
c |  |  |  |  | Doors 1340 clear)­
(D195) | IPU Bed Rooms with 1510w NFR leaves with hospital hinges | 1595 nom tbc | 1510 | 1486 tbc for 45 thick leaf | AS 1428.1 cl.13.2 re 850 clear opening |  | Requirement for LOBS in CCU, SOBS generally
a | For NBH to Healthscope requirements incl. hospital hinges | (1510 + 38 +38 +3 + 3 = 1592 actual tbc) |  |  | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs…
b
c
DOUBLE DOORS
D201 | L01 Mech DB Cafe |  | 600+600 x 2240h
D202 | L00 EDB |  | 650+650 x 2240h | 1029 NFR hinged
D215 | Double door | 1565 nom | 955 + 515 | 1295 transom closer pivot, (869 primary opening but 1563 set) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. | HFG RDS/ RLS for rms requiring 1400 clear. | Min. 450 secondary leaf required for slide arm closers. Wider leaf may be required for concealed closers that would probably be used in Mental Health for anti-ligature (540 for Dorma ITS 69) – check closer constraints for various types incl. RTS, ITS and TS and auto incl. sequencers.
| · corridor to GPC at NBH | (1555 hinged/ 1563 FR pivot actual) |  | 1363 hinged FD, (899 primary opening; 1580 set) | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit | 910 primary clear opening is required in certain HFG RDS/ RLS – not achieved if FR hinged or if transom pivot configuration | RNSH: had to use min.800+920 leaves to fit ITS closers and NE latches to PEC doors
|  |  |  | 1379 NFR hinged, (911 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Min. 720w leaf to fit transom closer, shear lock and reed switch (though achieved 620w on RNSH for door 07/1064)
[5 empty] | HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms |  | Min. 725w leaves to fit auto swing door operator but may need to add additional width for EMLs.
Min. WL of 530 where D = 900 in AS1428.1 requires min. 389w secondary leaf if hinged configuration assuming 100 nib, but this is too narrow for closer
[5 empty] | HFG cl. 710.27.00 re 1000 for hoists and shower trolleys |  | If sequencer is required, it will need to be integral with closers due to width of secondary leaf
(FYI) | Double door – Non-fire rated, 40 thick leaves and hinged configuration only | 1430 nom for hinged only | 955 + 390 | FYI: 1170 transom closer pivot, (869 primary opening but 1438 set) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. | HFG RDS/ RLS for rms requiring 1400 clear.
| (min. 1250 clear if NRF) | (1430 hinged/ 1438 FR pivot actual) | (minimal leaf widths to give 1250/ 910 clearances would be 954 + 387 leaves) | FYI: 1238 hinged FD, (899 primary opening; 1430 set) | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit |  | RNSH: NB. Bariatric bed is 1130 wide (add 100 for side rails ie 1230 wide) – check corridor width needed to suit turning circle. See email 10:27am on 24.11.08 JW to NL 1.07 – is a 1601 clear opening needed?
| · Horizontal exit in a patient care area under BCA min. 1250 clear |  |  | 1254 NFR hinged, (911 primary opening) | BCA cl.D3.2(e) re min.850 primary opening |  | Min. 450 secondary leaf required for slide arm closers. Wider leaf may be required for concealed closers that would probably be used in Mental Health for anti-ligature (540 for Dorma ITS 69) – check closer constraints for various types incl. RTS, ITS and TS and auto incl. sequencers.
| · access for hoists and shower trolleys |  |  |  | HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms
| · access for stretchers, large trolleys, large equipment, beds but check std and bariatric beds esp. if off 1800 clear corr | [5 empty] | RNSH: had to use min.800+920 leaves to fit ITS closers and NE latches to PEC doors
| · patient bed rooms, patient assisted bathrooms |  |  |  | HFG cl. 710.27.00 re 1000 for hoists and shower trolleys |  | Min. WL of 530 where D = 900 in AS1428.1 requires min. 389w secondary leaf if hinged configuration assuming 100 nib, but this is too narrow for closer
| · bed accessible rooms eg imaging rooms | [5 empty] | If sequencer is required, it will need to be integral with closers due to width of secondary leaf
Review for MCR: Unlikely to suit bariatric beds
| 6-Brick opening (1450 brick opening) | 1430 nom | 910 + 435 | 1238 hinged FD (854 primary opening) | BCA cl. D1.6 (f)(v) re 750 clear opening |  | Need to check if closer can fit on narrow secondary leaf (min 460 typically required)
| Allow 10mm tolerance each side | (1430 hinged) |  | 1254 NFR hinged (866 primary opening) | AS 1428.1 cl.13.2 re 850 clear opening (requires min 34 nib for WL to primary leaf) |  | Based on FFL being 40 below top of base course (to allow for sill and sub sill), 20mm at head for steel lintel and building tolerance
| · compliant for wheelchair access |  |  |  | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs |  | · 25C high = 2153, achieves 2030 clear door opening ht for FD
| · possibly to NBH L00 south near Dialysis | [5 empty] | · 26C high = 2239, achieves 2116 clear door opening ht for FD
· 27C high = 2324, achieves 2201 clear door opening ht for FD
· 28C high = 2410, achieves 2287 clear door opening ht for FD
D219 | Double door | 1565 nom | 735 +735 | 1295 transom closer pivot, (649 primary opening but 1563 set)
| · Cupboard GPC and ICU | (1555 hinged/ 1563 FR pivot actual) |  | 1363 hinged FD, (679 primary opening; 1 set) | Not applicable for circulation (non-compliant with BCA re min750 clear)
1379 NFR hinged, (691 primary opening)
D231 | Double door (min.1400 clear) | 1605 nom | 755 + 755 | 1335 transom closer pivot, (669 primary opening) | Not applicable for circulation (non-compliant with BCA re min750 clear)
| · Cupboard ICU | (1595 hinged/ 1603 FR pivot actual) |  | 1403 hinged FD, (699 primary opening)
1419 NFR hinged, (711 primary opening)
D232 tbc | Double door (min. 1400 clear) | 1605 nom | 920 + 590 | 1335 transom closer pivot, (834 primary opening) | BCA cl. D1.6 (f)( i )(A) re 1200 clear for doorway in patient care area through which patients would normally be transported in beds off corridor less than 2200 clear. Primary opening to be min. 800 clear. | BCA cl.D3.2(e) re min.850 primary opening | Used on RNSH for I Bed Rms in IPUs due to problems with Ensuite door swings
(old RNSH D20a) | · Horizontal exit in a patient care area under BCA min. 1250 clear | (1595 hinged/ 1603 FR pivot actual) |  | 1403 hinged FD, (864 primary opening) | BCA cl. D1.6 (f)(ii) re min. 1250 clear horizontal exit
| · access for hoists and shower trolleys |  |  | 1419 NFR hinged, (876 primary opening) | HFG cl. 710.25.00 re min. 1200 clear to inpatient bed rooms
· access for stretchers, large trolleys, large equipment, beds but check std and bariatric beds esp. if off 1800 clear corr
| · patient bed rooms, patient assisted bathrooms |  |  |  | HFG cl. 710.27.00 re 1000 for hoists and shower trolleys
· bed accessible rooms eg imaging rooms
| 7-Brick opening (1690 brick opening) | 1670 nom | 965 + 620 | 1478 hinged FD (913 primary opening) | BCA cl. D1.6 (f)(v) re 750 clear opening |  | Based on FFL being 30 below top of base course (to allow for sill and sub sill), 20mm at head for steel lintel and building tolerance
| Allow 10mm tolerance each side | (1670 hinged) |  | 1494 NFR hinged (921 primary opening) | AS 1428.1 cl.13.2 re 850 clear opening (requires min 34 nib for WL to primary leaf) |  | · 25C high = 2153, achieves 2040 clear door opening ht for FD
| · compliant for wheelchair access |  |  |  | HFG cl. 710.27.00 requires min. 900 clear for wheelchairs |  | · 26C high = 2239, achieves 2126 clear door opening ht for FD
| · possibly to NBH B01 near MTY | [5 empty] | · 27C high = 2324, achieves 2211 clear door opening ht for FD
· 28C high = 2410, achieves 2297 clear door opening ht for FD
D24? | Double door (min. 1500 clear in FR hinged and NFR hinged) | 1735 nom | 990 + 650 |  | BCA cl.D3.2(e) re min.850 primary opening |  | 650 is non-standard leaf
910 primary clear opening is required in certain HFG RDS/ RLS
D24?? | Double door (min. 1500 clear in FR hinged and NFR hinged) | (1725 hinged/ 1733 FR pivot actual) | 970 + 670 |  | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts | 670 is non-standard leaf
Would need 990w primary leaf to achieve 910 clear for transom pivot
910 primary clear opening not achieved for transom pivot configuration for 970w leaf.
(910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts.)
D24??? | Double door (min. 1500 clear in FR hinged and NFR hinged) | 1735 nom | 920 + 720 | 1465 transom closer pivot, (834 primary opening) | As for D230 above | HFG RDS/ RLS for Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms – check other specialist rms requiring 1500 clear. Non-compliance if transom closer configuration which is unlikely in these contexts.
(old RNSH D21) | · Suitable for use as door across 1800 clear corridor | (1725 hinged/ 1733 FR pivot actual) |  | 1533 hinged FD, (868 primary opening) | HFG RDS/ RLS for Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms – check other specialist rms requiring1500 clear, except if transom closer is used |  | RNSH: NB. Bariatric bed is 1130 wide (add 100 for side rails ie 1230 wide) – check corridor width needed to suit turning circle. See email 10:27am on 24.11.08 JW to NL 1.07 – is a 1601 clear opening needed?
| · Preferable for use for bed access eg to bed rooms – check bariatric beds |  |  | 1549 NFR hinged, (876 primary opening)
| · Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms | [5 empty] | This is the min. combination of std leaf sizes as a double door.
To suit bed access off 1800 clear corridor but check suitability for bariatric beds
Cannot have 2 equal leaves @ 820 each as primary opening would not comply with BCA if in a patient care area through which patients would normally be transported in bed. See BCA cl. D1.6 (f)( i ) re 800 primary opening or BCA cl.D3.2(e) re min.850 primary opening
Review for MCR: Does this suit bariatric beds?
910 primary clear opening not achieved. 910 is required in certain HFG RDS/ RLS
D250 tbc | Double door (min. clear) | 1765 nom | 840 + 840 | 1573 hinged FD, (primary opening tba) |  |  | 2 x 1765 sets will suit nom. 3740 - 4000 w EDB cupboard
(old RNSH D21a) | · Suitable for EDB cupboards only | (1765 hinged actual) |  | 1589 NFR hinged, (primary opening tba) | TBA generally | TBA generally | (2 x 1765 + 190 block mullion = 2 x 10mm – 140mm nibs)
(FR pivot not used for EDB)
RNS Spec cl. 7.8.2 re 1 leaf to be min. 920 wide.
RNS Spec cl. 7.8.2 re double doors shall not be less than 1440 overall width of both leaves.
D251 | Comms Cupboards | 1765 nom | 840 + 840 x 2240h | 1573 hinged FD, (primary opening tba)
|  | (1765 hinged actual) |  | 1589 NFR hinged, (primary opening tba)
(FR pivot not used for EDB)
D261 | Double door (min.1500 clear) | 1785 nom | 845 + 845 | 1515 transom closer pivot, (759 primary opening) | Not applicable for circulation
| · Cupboard PAD | (1775 hinged/ 1783 FR pivot actual) |  | 1583 hinged FD, (793 primary opening)
1599 NFR hinged, (801 primary opening)
D261 | Double door (min. 1500 clear) | 1785 nom tbc | 970 + 720 x 2340h | 1515 transom closer pivot, (884 primary opening) | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts
D262 | · Suitable for use as door across 1800 clear corridor but will have 82.5mm nibs | (1775 hinged/ 1783 FR pivot actual) |  | 1583 hinged FD, (918 primary opening) |  |  | 910 primary clear opening not achieved for transom pivot configuration for 970w leaf.
| · Large Procedure Rms eg 20 sqm, ORs, Anaes, CT Scanning Procedure Rms |  |  | 1599 NFR hinged, (926 primary opening)
| · To suit bed access off 1800 clear corridor but check suitability for bariatric beds | [5 empty] | (910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts.)
970 leaf is also used in D270 below
4.4.12: This specially high door set is made for Ambulatory Care Precinct to visually open up the spaces near Waiting
D267 | Double door | 1905 nom | 990 + 820 | 1634 transom closer pivot, (904 primary opening) | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS but transom closers unlikely in room contexts
| · Corridors in MH | (1895 hinged/ 1903 FR pivot actual) |  | 1703 hinged FD, (938 primary opening)
1719 NFR hinged, (946 primary opening)
D271 | EDB Option tbc ( also see D281 below) | [5 empty] | As per D270 but 2240h leaves
UPS Rm
D271a (CHECK WITH JULIE) | Cafe Mech DB cupboard |  | 600 + 600 x 2240h |  |  |  | Amend BVN CAD cell name if this door is to be used.
D201 tbc
D272 | [6 empty] | As per D270 but 2340h leaves
D273 | [6 empty] | As per D270 but 2440h leaves
D277 | Double door (min. 1800 clear) | 2075 nom | 990 + 990 | 1805 transom closer pivot, (904 primary opening) | BCA cl.D3.2(e) re min.850 primary opening | 910 primary clear opening is required in certain HFG RDS/ RLS
De277? | · For Link Bridge for max clear opening on esp. hold open doors | (2065 hinged/ 2073 FR pivot actual) |  | 1873 hinged FD, (938 primary opening)
1889 NFR hinged, (946 primary opening)
D281 | Double door | 2235 nom | 1070 + 1070 x 2240h | 1965 transom closer pivot, (984 primary opening) | HFG RDS/ RLS for Catheter Lab Procedure Rms and Angio Procedure Rms – check other specialist rms requiring 1600 clear | 910 primary clear opening is required in certain HFG RDS/ RLS
| · EDB Option | (2225 hinged/ 2233 FR pivot actual) |  | 2033 hinged FD, (1018 primary opening) | BCA cl.D3.2(e) re min.850 primary opening
2049 NFR hinged, (1026 primary opening)
| Double door (min. 2115 clear) | 2385 nom | 1145 + 1145 | 2115 transom closer pivot, (1059 primary opening) | TBA | TBA | Face blockwork doorsets:
| · for face blockwork structural opening 2410. NB. See Remarks re hts | (2375 hinged/ 2383 FR pivot actual) |  | 2183 hinged FD, (1093 primary opening) |  |  | · for L00, allow say 2200 set ht in 2210h structural opening to avoid 2 courses of 90h blocks in limited wall ht
(old RNS D22c) |  |  |  | 2199 NFR hinged, (1101 primary opening) |  |  | Min. 45 thick to minimise bowing
| Double door (min. 2250 clear) | 2455 nom for hinged configuration only | 1180 + 1180 | (not calculated for transom closer) | 1.3.5 re min. 1400 clear opening to patient bed rooms |  | Assumes 40 thick NFR leaves.
(old RNSH D23) | · for AGV access to Disposal Rooms | (2445 hinged actual) |  | 2253 hinged FD, (1128 primary opening)
|  |  |  | 2269 NFR hinged, (1136 primary opening) |  |  | Need to confirm thickness with respect to bowing etc.
If FR pivot configuration used, doorset = 2453, giving 2187 clear opening transom closer pivot, (1094 primary opening)
NB RNSH cell should be 2453 nom in lieu of 2445
D290a-p | Double door |  | 1250 + 1250 x 2350h
· Rotunda pivot door (Jamie)
D290 | Double door |  | 1250 + 1250 x 2240h | 2409 NFR hinged
D291 | Double door |  | 1250 + 1250 x 2240h | 2409 NFR hinged
· L00 EDB